## Intrados-Extrados
Table 1.1 Summary of MS pipe, HR Pipe | [16 empty] | Constants |  |  |  | Intrados | Extrados | Intrados Thickness (mm) | Extrados Thickness (mm) | Intrados Thickness (mm) | Extrados Thickness (mm)
No. | Name | Materials | (Minimum inner diameter × minimum wall thickness mm) | ID | th. | ØD | Inner diameter deviation(mm) | Wall thickness deviation(mm) | Average single weight (kg/m) | Ovality | Weight deviation | Quantity (m) | Material standards | Design Pressure (Mpa) | Design Temperature (°C) | Allowable Stress Values (Mpa) | E Weld Joint Quality Factor | y Coefficient | A Additional Thickness | R=1,5D Bending Radius
1 | Main-steam pipe | A335 P92 | ID (311x88) | 311 | 88 | 487 | +3.175/-0 | +3.5/-0 | 891 | ≤1.5% | -5%, +5% | 605 | ASME | 31.34 | 608.1 | 68.2 | 1 | 0.7 | 2 | 730.5 | 1.25 | 0.875 | 99.758 | 78.4039 | 111.3062 | 74.0162
2 | HP bypass inlet pipe | A335 P92 | ID (235X68) | 235 | 88 | 411 | +2.36/-0 | +2.0/-0 | 520 | ≤1.5% | -5%, +5% | 8 | ASME | 31.43 | 608.1 | 68.2 | 1 | 0.7 | 2 | 616.5 | 1.25 | 0.875 | 84.3623 | 66.6249 | 85.2218 | 56.8193
3 | HP bypass inlet pipe (branch) | A335 P92 | ID (165X49) | 165 | 49 | 263 | +2.36/-0 | +2.0/-0 | 267 | ≤1.5% | -5%, +5% | 33 | ASME | 31.43 | 608.1 | 68.2 | 1 | 0.7 | 2 | 394.5 | 1.25 | 0.875 | 53.9837 | 43.3537 | 60.8472 | 40.7635
4 | HR steam main pipe | A335 P92 | ID (813×56) | 813 | 56 | 925 | +4.75/-0 | +3.8/-0 | 1248 | ≤1.5% | -5%, +5% | 173 | ASME | 7.34 | 617 | 60.61 | 1 | 0.7 | 2 | 1387.5 | 1.25 | 0.875 | 63.3042 | 47.6243 | 66.7796 | 46.7077
5 | HR steam branch pipe(Include the LP bypass inlet main pipe) | A335 P92 | ID (578×41) | 578 | 41 | 660 | +3.962/-0 | +2.8/-0 | 651 | ≤1.5% | -5%, +5% | 218 | ASME | 7.34 | 617 | 60.61 | 1 | 0.7 | 2 | 990 | 1.25 | 0.875 | 45.1684 | 34.5536 | 48.1466 | 33.8481
6 | LP bypass inlet branch pipe | A335 P92 | ID (400×29) | 400 | 29 | 458 | +3.175/-0 | +2.5/-0 | 322 | ≤1.5% | -5%, +5% | 47 | ASME | 7.34 | 617 | 60.61 | 1 | 0.7 | 2 | 687 | 1.25 | 0.875 | 31.3441 | 24.5902 | 34.033 | 24.1076
Table 1.2 Summary Table of CR pipe, BFW pipe, LP Bypass Outlet Pipes, No.1 extraction steam pipe
7 | CR steam main pipe | A672B70CL32 | ∅864X30.18 | 803.64 | 30.18 | 864 | ±0.5% | -0.3mm | 621 | <1% | / | 150 | ASME | 7.34 | 378.5 | 118.693 | 1 | 0.7 | 2 | 1296 | 1.25 | 0.875 | 31.6795 | 24.5225 | 33.9565 | 24.2113
8 | CR steam branch (boiler side) | A672B70CL32 | ∅610X22.23 | 565.54 | 22.23 | 610 | ±0.5% | -0.3mm | 322 | <1% | / | 170 | ASME | 7.34 | 378.5 | 118.693 | 1 | 0.7 | 2 | 915 | 1.25 | 0.875 | 22.3663 | 17.9013 | 24.5354 | 17.6632
9 | HP bypass valve outlet pipe (mixing temperature section) | A691Gr.91rCL42 | ∅711X25.4 | 660.2 | 25.4 | 711 | ±0.5% | -0.3mm | 429 | <1% | / | 8 | ASME | 7.24 | 378.5 | 156.581 | 1 | 0.7 | 2 | 1066.5 | 1.25 | 0.875 | 19.7481 | 15.9868 | 21.5333 | 15.6013
10 | Outlet pipe of HP bypass | A672B70CL32 | ∅711X25.4 | 660.2 | 25.4 | 711 | ±0.5% | -0.3mm | 429 | <1% | / | 11.5 | ASME | 7.24 | 378.5 | 118.693 | 1 | 0.7 | 2 | 1066.5 | 1.25 | 0.875 | 25.7324 | 20.2907 | 27.9144 | 20.0136
11 | Outlet pipe of LP bypass | A691Gr.91CL42 | ∅1016X15 | 986 | 15 | 1016 | ±0.5% | -0.3mm | 370 | <1% | / | 13 | ASME | 0.9 | 175 | 167.199 | 1 | 0.7 | 2 | 1524 | 1.25 | 0.875 | 3.4021 | 4.3848 | 5.3373 | 4.3347
12 | No.1 extraction steam pipe | A335P22 | ∅219.1X12.7 | 193.7 | 12.7 | 219.1 | ±0.5% | -0.3mm | 64.6 | <1% | / | 77.5 | ASME | 10.1 | 425 | 114.4537 | 1 | 0.7 | 2 | 328.65 | 1.25 | 0.875 | 11.2179 | 10.0251 | 13.277 | 9.8137
13 | No.2 extraction steam pipe | A106B | ∅323.9X14.27 | 295.36 | 14.27 | 323.9 | ±0.5% | -0.3mm | 109 | <1% | / | 83.5 | ASME | 7.34 | 378.6 | 102.7904 | 1 | 0.7 | 2 | 485.85 | 1.25 | 0.875 | 13.6055 | 11.6949 | 15.7279 | 11.5309
14 | No.3 extraction steam pipe | A335P22 | ∅355.6X8.74 | 338.12 | 8.74 | 355.6 | ±0.5% | -0.3mm | 74.8 | <1% | / | 103.5 | ASME | 2.71 | 487.9 | 89.982 | 1 | 0.7 | 2 | 533.4 | 1.25 | 0.875 | 6.5217 | 6.6006 | 8.5134 | 6.5438
15 | No.3 extraction steam pipe | A106B | ∅323.9X7.14 | 309.62 | 7.14 | 323.9 | ±0.5% | -0.3mm | 55.8 | <1% | / | 136 | ASME | 2.71 | 322.8 | 117.901 | 1 | 0.7 | 2 | 485.85 | 1.25 | 0.875 | 4.5614 | 5.212 | 6.5446 | 5.1729
16 | No.4 extraction steam pipe | A672B70CL32 | ∅660X7.92 | 644.16 | 7.92 | 660 | ±0.5% | -0.3mm | 127.4 | <1% | / | 65(HOLD) | ASME | 1.1 | 362.4 | 126.2743 | 1 | 0.7 | 2 | 990 | 1.25 | 0.875 | 3.5662 | 4.502 | 5.5405 | 4.4759
17 | No.4 extraction steam pipe | A672B70CL32 | ∅457X6.35 | 444.3 | 6.35 | 457 | ±0.5% | -0.3mm | 70.6 | <1% | / | 56(HOLD) | ASME | 1.1 | 362.4 | 126.2743 | 1 | 0.7 | 2 | 685.5 | 1.25 | 0.875 | 2.4693 | 3.7325 | 4.4488 | 3.7125
18 | BFW pipe | 15NiCuMoNb5-6-4 | ∅508x55 | 398 | 55 | 508 | ±1.0% | +15% -12.5% | 614 | <1% | / | 446(HOLD) | EN10216-2 | 39.83 | 307.1 | 203.3 | 1 | 0.7 | 2 | 762 | 1.25 | 0.875 | 53.1008 | 40.8774 | 55.1275 | 38.3251
19 | BFW branch pipe 1 | 15NiCuMoNb5-6-4 | ∅355.6x40 | 275.6 | 40 | 355.6 | ±1.0% | +15% -12.5% | 311 | <1% | / | 140(HOLD) | EN10216-3 | 39.83 | 307.1 | 203.3 | 1 | 0.7 | 2 | 533.4 | 1.25 | 0.875 | 37.1706 | 29.2142 | 38.9513 | 27.2649
20 | BFW branch pipe 2 | 15NiCuMoNb5-6-4 | ∅273x30 | 213 | 30 | 273 | ±0.9% | +12.5% -12.5% | 180 | <1% | / | 115(HOLD) | EN10216-4 | 39.83 | 307.1 | 203.3 | 1 | 0.7 | 2 | 409.5 | 1.25 | 0.875 | 28.5365 | 22.8928 | 30.6783 | 21.6083
21 | BFW branch pipe 3 | 15NiCuMoNb5-6-4 | ∅355.6x40 | 275.6 | 40 | 355.6 | ±1.0% | +15% -12.5% | 311 | <1% | / | 40(HOLD) | EN10216-5 | 39.83 | 307.1 | 203.3 | 1 | 0.7 | 2 | 533.4 | 1.25 | 0.875 | 37.1706 | 29.2142 | 38.9513 | 27.2649
22 | BFW branch pipe 4 (from BFP outlet to stop valve) | 15NiCuMoNb5-6-4 | ∅355.6x45 | 265.6 | 45 | 355.6 | ±1.0% | +15% -12.5% | 345 | <1% | / | 132(HOLD) | EN10216-6 | 39.83 | 307.1 | 203.3 | 1 | 0.7 | 2 | 533.4 | 1.25 | 0.875 | 37.1706 | 29.2142 | 37.6298 | 26.3613
23 | BFW branch pipe 5 | 15NiCuMoNb5-6-4 | ∅323.9x36 | 251.9 | 36 | 323.9 | ±1.0% | +15% -12.5% | 256 | <1% | / | 28(HOLD) | EN10216-7 | 39.83 | 307.1 | 203.3 | 1 | 0.7 | 2 | 485.85 | 1.25 | 0.875 | 33.857 | 26.7882 | 35.8192 | 25.1234
24 | Recirculating BFW pipe | 15NiCuMoNb5-6-4 | ∅219.1x28 | 163.1 | 28 | 219.1 | ±0.9% | -0.3mm | 132 | <1% | / | 190(HOLD) | EN10216-8 | 42.88 | 184 | 203.3 | 1 | 0.7 | 2 | 328.65 | 1.25 | 0.875 | 24.3829 | 19.9049 | 25.9199 | 18.3233
Taken from ASME B31.1 Power Piping Edition 2010
Taken form RFQ

## Intrados-Extrados (2)
Table 1.2 Summary Table of CR pipe, BFW pipe, LP Bypass Outlet Pipes, No.1 extraction steam pipe | [16 empty] | Constants |  |  |  | Intrados | Extrados | Intrados Thickness (mm) | Extrados Thickness (mm) | Intrados Thickness (mm) | Extrados Thickness (mm)
No. | Name | Materials | (Minimum inner diameter × minimum wall thickness mm) | ID | th. | ØD | Inner diameter deviation(mm) | Wall thickness deviation(mm) | Average single weight (kg/m) | Ovality | Weight deviation | Quantity (m) | Material standards | Design Pressure (Mpa) | Design Temperature (°C) | Allowable Stress Values (Mpa) | E Weld Joint Quality Factor | y Coefficient | A Additional Thickness | R=1,5D Bending Radius
1 | Main-steam pipe | A335 P92 | ID (311x88) | 311 | 88 | 487 | +3.175/-0 | +3.5/-0 | 891 | ≤1.5% | -5%, +5% | 605 | ASME | 31.34 | 608.1 | 70.36 | 1 | 0.7 | 0 | 730.5 | 1.25 | 0.875 | 97.5544 | 74.5611 | 103.9408 | 68.6299
2 | HP bypass inlet pipe | A335 P92 | ID (235X68) | 235 | 88 | 411 | +2.36/-0 | +2.0/-0 | 520 | ≤1.5% | -5%, +5% | 8 | ASME | 31.43 | 608.1 | 70.36 | 1 | 0.7 | 0 | 616.5 | 1.25 | 0.875 | 82.5003 | 63.0672 | 78.8114 | 52.0273
3 | HP bypass inlet pipe (branch) | A335 P92 | ID (165X49) | 165 | 49 | 263 | +2.36/-0 | +2.0/-0 | 267 | ≤1.5% | -5%, +5% | 33 | ASME | 31.43 | 608.1 | 70.36 | 1 | 0.7 | 0 | 394.5 | 1.25 | 0.875 | 52.7922 | 40.3569 | 55.3357 | 36.5298
4 | HR steam main pipe | A335 P92 | ID (813×56) | 813 | 56 | 925 | +4.75/-0 | +3.8/-0 | 1248 | ≤1.5% | -5%, +5% | 173 | ASME | 7.34 | 617 | 63.06 | 1 | 0.7 | 0 | 1387.5 | 1.25 | 0.875 | 61.072 | 43.9697 | 61.8437 | 42.7058
5 | HR steam branch pipe(Include the LP bypass inlet main pipe) | A335 P92 | ID (578×41) | 578 | 41 | 660 | +3.962/-0 | +2.8/-0 | 651 | ≤1.5% | -5%, +5% | 218 | ASME | 7.34 | 617 | 63.06 | 1 | 0.7 | 0 | 990 | 1.25 | 0.875 | 43.5757 | 31.373 | 43.9676 | 30.3616
6 | LP bypass inlet branch pipe | A335 P92 | ID (400×29) | 400 | 29 | 458 | +3.175/-0 | +2.5/-0 | 322 | ≤1.5% | -5%, +5% | 47 | ASME | 7.34 | 617 | 63 | 1 | 0.7 | 0 | 687 | 1.25 | 0.875 | 30.265 | 21.7903 | 30.4577 | 21.0321
Table 1.2 Summary Table of CR pipe, BFW pipe, LP Bypass Outlet Pipes, No.1 extraction steam pipe
7 | CR steam main pipe | A672B70CL32 | ∅864X30.18 | 803.64 | 30.18 | 864 | ±0.5% | -0.3mm | 621 | <1% | / | 150 | ASME | 7.34 | 378.5 | 118.693 | 1 | 0.7 | 0 | 1296 | 1.25 | 0.875 | 31.6795 | 22.5225 | 31.7982 | 22.1013
8 | CR steam branch (boiler side) | A672B70CL32 | ∅610X22.23 | 565.54 | 22.23 | 610 | ±0.5% | -0.3mm | 322 | <1% | / | 170 | ASME | 7.34 | 378.5 | 118.693 | 1 | 0.7 | 0 | 915 | 1.25 | 0.875 | 22.3663 | 15.9013 | 22.3771 | 15.5532
9 | HP bypass valve outlet pipe (mixing temperature section) | A691Gr.91rCL42 | ∅711X25.4 | 660.2 | 25.4 | 711 | ±0.5% | -0.3mm | 429 | <1% | / | 8 | ASME | 7.24 | 378.5 | 156.581 | 1 | 0.7 | 0 | 1066.5 | 1.25 | 0.875 | 19.7481 | 13.9868 | 19.4156 | 13.5194
10 | Outlet pipe of HP bypass | A672B70CL32 | ∅711X25.4 | 660.2 | 25.4 | 711 | ±0.5% | -0.3mm | 429 | <1% | / | 11.5 | ASME | 7.24 | 378.5 | 118.693 | 1 | 0.7 | 0 | 1066.5 | 1.25 | 0.875 | 25.7324 | 18.2907 | 25.7584 | 17.9051
11 | Outlet pipe of LP bypass | A691Gr.91CL42 | ∅1016X15 | 986 | 15 | 1016 | ±0.5% | -0.3mm | 370 | <1% | / | 13 | ASME | 0.9 | 175 | 167.199 | 1 | 0.7 | 0 | 1524 | 1.25 | 0.875 | 3.4021 | 2.3848 | 3.3239 | 2.3253
12 | No.1 extraction steam pipe | A335P22 | ∅219.1X12.7 | 193.7 | 12.7 | 219.1 | ±0.5% | -0.3mm | 64.6 | <1% | / | 77.5 | ASME | 10.1 | 425 | 114.4537 | 1 | 0.7 | 0 | 328.65 | 1.25 | 0.875 | 11.2179 | 8.0251 | 11.0488 | 7.6556
13 | No.2 extraction steam pipe | A106B | ∅323.9X14.27 | 295.36 | 14.27 | 323.9 | ±0.5% | -0.3mm | 109 | <1% | / | 83.5 | ASME | 7.34 | 378.6 | 102.7904 | 1 | 0.7 | 0 | 485.85 | 1.25 | 0.875 | 13.6055 | 9.6949 | 13.5445 | 9.4035
14 | No.3 extraction steam pipe | A335P22 | ∅355.6X8.74 | 338.12 | 8.74 | 355.6 | ±0.5% | -0.3mm | 74.8 | <1% | / | 103.5 | ASME | 2.71 | 487.9 | 89.982 | 1 | 0.7 | 0 | 533.4 | 1.25 | 0.875 | 6.5217 | 4.6006 | 6.4372 | 4.4907
15 | No.3 extraction steam pipe | A106B | ∅323.9X7.14 | 309.62 | 7.14 | 323.9 | ±0.5% | -0.3mm | 55.8 | <1% | / | 136 | ASME | 2.71 | 322.8 | 117.901 | 1 | 0.7 | 0 | 485.85 | 1.25 | 0.875 | 4.5614 | 3.212 | 4.4866 | 3.1325
16 | No.4 extraction steam pipe | A672B70CL32 | ∅660X7.92 | 644.16 | 7.92 | 660 | ±0.5% | -0.3mm | 127.4 | <1% | / | 65(HOLD) | ASME | 1.1 | 362.4 | 126.2743 | 1 | 0.7 | 0 | 990 | 1.25 | 0.875 | 3.5662 | 2.502 | 3.5186 | 2.4606
17 | No.4 extraction steam pipe | A672B70CL32 | ∅457X6.35 | 444.3 | 6.35 | 457 | ±0.5% | -0.3mm | 70.6 | <1% | / | 56(HOLD) | ASME | 1.1 | 362.4 | 126.2743 | 1 | 0.7 | 0 | 685.5 | 1.25 | 0.875 | 2.4693 | 1.7325 | 2.4269 | 1.6972
18 | BFW pipe | 15NiCuMoNb5-6-4 | ∅508x55 | 398 | 55 | 508 | ±1.0% | +15% -12.5% | 614 | <1% | / | 446(HOLD) | EN10216-2 | 39.83 | 307.1 | 203.3 | 1 | 0.7 | 0 | 762 | 1.25 | 0.875 | 53.1008 | 38.8774 | 52.5988 | 35.9637
19 | BFW branch pipe 1 | 15NiCuMoNb5-6-4 | ∅355.6x40 | 275.6 | 40 | 355.6 | ±1.0% | +15% -12.5% | 311 | <1% | / | 140(HOLD) | EN10216-3 | 39.83 | 307.1 | 203.3 | 1 | 0.7 | 0 | 533.4 | 1.25 | 0.875 | 37.1706 | 27.2142 | 36.4227 | 24.9035
20 | BFW branch pipe 2 | 15NiCuMoNb5-6-4 | ∅273x30 | 213 | 30 | 273 | ±0.9% | +12.5% -12.5% | 180 | <1% | / | 115(HOLD) | EN10216-4 | 39.83 | 307.1 | 203.3 | 1 | 0.7 | 0 | 409.5 | 1.25 | 0.875 | 28.5365 | 20.8928 | 28.1496 | 19.2469
21 | BFW branch pipe 3 | 15NiCuMoNb5-6-4 | ∅355.6x40 | 275.6 | 40 | 355.6 | ±1.0% | +15% -12.5% | 311 | <1% | / | 40(HOLD) | EN10216-5 | 39.83 | 307.1 | 203.3 | 1 | 0.7 | 0 | 533.4 | 1.25 | 0.875 | 37.1706 | 27.2142 | 36.4227 | 24.9035
22 | BFW branch pipe 4 (from BFP outlet to stop valve) | 15NiCuMoNb5-6-4 | ∅355.6x45 | 265.6 | 45 | 355.6 | ±1.0% | +15% -12.5% | 345 | <1% | / | 132(HOLD) | EN10216-6 | 39.83 | 307.1 | 203.3 | 1 | 0.7 | 0 | 533.4 | 1.25 | 0.875 | 37.1706 | 27.2142 | 35.1011 | 23.9999
23 | BFW branch pipe 5 | 15NiCuMoNb5-6-4 | ∅323.9x36 | 251.9 | 36 | 323.9 | ±1.0% | +15% -12.5% | 256 | <1% | / | 28(HOLD) | EN10216-7 | 39.83 | 307.1 | 203.3 | 1 | 0.7 | 0 | 485.85 | 1.25 | 0.875 | 33.857 | 24.7882 | 33.2906 | 22.7619
24 | Recirculating BFW pipe | 15NiCuMoNb5-6-4 | ∅219.1x28 | 163.1 | 28 | 219.1 | ±0.9% | -0.3mm | 132 | <1% | / | 190(HOLD) | EN10216-8 | 42.88 | 184 | 203.3 | 1 | 0.7 | 0 | 328.65 | 1.25 | 0.875 | 24.3829 | 17.9049 | 23.3473 | 15.9326
Taken from ASME B31.1 Power Piping Edition 2010
Taken form RFQ

## CSEPDI-ASME Stress Values
MAXIMUM ALLOWABLE STRESS VALUES
No | Name | Material | Design Temp.(ºC) | Design Fahrenheit(F) |  | CSEPDI (RFQ) |  |  | ASME (from ksi to Mpa)
[5 empty] | Temp. (°C) | 600 | 610 | 608.1 | 600 | 625 | 608.1
1 | Main-steam pipe | A335 P92 | 608.1 | 1126.58 | Allow. Stress (Mpa) | 75.3 | 66.7 | 68.2 | 77 | 56.5 | 70.358
2 | HP bypass inlet pipe | A335 P92 | 608.1 | 1126.58 |  |  |  | 68.2 |  |  | 70.358
3 | HP bypass inlet pipe (branch) | A335 P92 | 608.1 | 1126.58 |  |  |  | 68.2 |  |  | 70.358
4 | HR steam main pipe | A335 P92 | 617 | 1142.6 | Temp. (°C) | 610 | 620 | 617 | 600 | 625 | 617
[5 empty] | Allow. Stress (Mpa) | 66.7 | 58 | 60.61 | 77 | 56.5 | 63.06
1 | HR steam branch pipe (Include the LP bypass inlet main pipe) | A335 P92 | 617 | 1142.6 |  |  |  | 60.61 |  |  | 63.06
2 | LP bypass inlet branch pipe | A335 P92 | 617 | 1142.6 |  |  |  | 60.61 |  |  | 63.06
3 | CR steam main pipe | A672B70CL32 | 378.5 | 713.3 | Temp. (°C) | 371 | 399 | 378.5 | 371 | 399 | 378.5
[5 empty] | Allow. Stress (Mpa) | 124.8 | 102 | 118.69 | 124.8 | 102 | 118.69
4 | CR steam branch (boiler side) | A672B70CL32 | 378.5 | 713.3 |  |  |  |  | 700,00 F ° | 750 F° | 118.743
[9 empty] | 18,1ksi | 14,8ksi | 118.743
5 | HP bypass valve outlet pipe (mixing temperature section) | A691Gr.91CL42 | 378.5 | 713.3 | Temp. (°C) |  |  |  | 371.11 | 398.89 | 378.5
[5 empty] | Allow. Stress (Mpa) |  |  |  | 157.89 | 153.06 | 156.64
6 | Outlet pipe of HP bypass | A672B70CL32 | 378.5 | 713.3 |  |  |  | 118.693 |  |  | 118.743
7 | Outlet pipe of LP bypass | A691Gr.91CL42 | 175 | 347 | Temp. (°C) |  |  |  | 700,00 F ° | 750 F° | 156.6351
[5 empty] | Allow. Stress (Mpa) |  |  |  | 18,1ksi | 14,8ksi
8 | No.1 extraction steam pipe | A335P22 | 425 | 797 | Temp. (°C) |  |  |  | 398.89 | 426.67 | 425
[5 empty] | Allow. Stress (Mpa) |  |  |  | 114.45 | 114.45 | 114.45
9 | No.2 extraction steam pipe | A106B | 378.6 | 713.48 | Temp. (°C) |  |  |  | 371.11 | 398.89 | 378.6
[5 empty] | Allow. Stress (Mpa) |  |  |  | 107.56 | 89.63 | 102.66
10 | No.3 extraction steam pipe | A335P22 | 487.9 | 910.22 |  |  |  | 89.982 |  |  | 89.91
11 | No.3 extraction steam pipe | A106B | 322.8 | 613.04 | Temp. (°C) |  |  |  | 311.56 | 343.33 | 322.8
[5 empty] | Allow. Stress (Mpa) |  |  |  | 117.9 | 117.9 | 117.9
12 | No.4 extraction steam pipe | A672B70CL32 | 362.4 | 684.32 |  |  |  | 126.2743 |  |  | 126.3395
13 | No.4 extraction steam pipe | A672B70CL32 | 362.4 | 684.32 |  |  |  | 126.2743 |  |  | 126.3395
14 | BFW pipe | 15NiCuMoNb5-6-4 | 307.1 | 584.78 | Temp. (°C) | 300 | 350 | 307.1
[5 empty] | Allow. Stress (Mpa) | 203.3 | 203.3 | 203.3
15 | BFW branch pipe 1 | 15NiCuMoNb5-6-4 | 307.1 | 584.78 | Allow. Stress (Mpa) | 203.3 | 203.3 | 203.3 |  |  | 183.4
16 | BFW branch pipe 2 | 15NiCuMoNb5-6-4 | 307.1 | 584.78 |  |  |  | 203.3 |  |  | 183.4
17 | BFW branch pipe 3 | 15NiCuMoNb5-6-4 | 307.1 | 584.78 |  |  |  | 203.3 |  |  | 183.4
18 | BFW branch pipe 4 (from BFP outlet to stop valve) | 15NiCuMoNb5-6-4 | 307.1 | 584.78 |  |  |  | 203.3 |  |  | 183.4
19 | BFW branch pipe 5 | 15NiCuMoNb5-6-4 | 307.1 | 584.78 |  |  |  | 203.3 |  |  | 183.4
20 | Recirculating BFW pipe | 15NiCuMoNb5-6-4 | 184 | 363.2 |  |  |  | 203.3 |  |  | 183.4

## A335 P92 Intp.
600 | 77 | 600 | 77
608.1 | 70.358 | 617 | 63.06
625 | 56.5 | 625 | 56.5

## A672B70CL32 Int.
T(°F) = T(°C) × 9/5 + 32
| 713.3 | 378.5
371.1111 | 700 | 18.1
378.5 | 713.3 | 17.2222 | ksi | 118.7429 | Mpa
398.8889 | 750 | 14.8 |  | 102.0424
0
343.3333 | 650 | 18.8 |  | 129.6214
362.2222 | 684 | 18.324 | ksi | 126.3395 | Mpa
371.1111 | 700 | 18.1 |  | 124.7951

## A691Gr.91CL42 Int.
T(°F) = T(°C) × 9/5 + 32
| 713.3 | 378.5
371.1111 | 700 | 22.9 |  | 157.8899
378.5 | 713.3 | 22.718 | ksi | 156.6351 | Mpa
398.8889 | 750 | 22.2 |  | 153.0636

## A335P22 Int.
T(°F) = T(°C) × 9/5 + 32
| 797 | 425
| 910.22 | 487.9
398.8889 | 750 | 16.6 |  | 114.453
425 | 797 | 16.6 | ksi | 114.453 | Mpa
426.6667 | 800 | 16.6 |  | 114.453
-17.7778 |  |  |  | 0
482.2222 | 900 | 13.6 |  | 93.7687
487.7778 | 910 | 13.04 |  | 89.9076 | Mpa
510 | 950 | 10.8 |  | 74.4634

## A106B
T(°F) = T(°C) × 9/5 + 32
| 713.48 | 378.6
| 613.04 | 322.8
315.5556 | 600 | 17.1 |  | 117.9003
322.8 | 613.04 | 17.1 | ksi | 117.9003 | Mpa
343.3333 | 650 | 17.1 |  | 117.9003
-17.7778
371.1111 | 700 | 15.6 |  | 107.5582
378.6 | 713.48 | 14.89 |  | 102.6629 | Mpa
398.8889 | 750 | 13 |  | 89.6318

## 15NiCuMoNb5-6-4(A335 P36 Cl.2)
T(°F) = T(°C) × 9/5 + 32
584.78 | 307.1
363.2 | 184
300 | 26.6
363.2 | 26.6 | ksi | 183.4005 | Mpa
400 | 26.6
500 | 26.6
584.78 | 26.6 |  | 183.4005 | Mpa
600 | 26.6